## PPM schedule
docket.
Site | Asset | Task | Frequency | Standard or regulation | Last done | Next due | Contractor | Notes
Example House | Fire alarm panel | Weekly call point test | Weekly | BS 5839-1 |  |  | In house | Test a different call point each week
Example House | Fire alarm system | Service and inspection | Every 6 months | BS 5839-1
Example House | Emergency lighting | Monthly functional test | Monthly | BS 5266-1 |  |  | In house | Short flick test
Example House | Emergency lighting | Full duration test | Annually | BS 5266-1
Example House | Fire extinguishers | Visual check | Monthly | BS 5306-3 |  |  | In house
Example House | Fire extinguishers | Service | Annually | BS 5306-3
Example House | Gas boiler | Service and safety check | Annually (typical) | Manufacturer's instructions and Gas Safety (Installation and Use) Regulations 1998 |  |  |  | Gas Safe registered engineer. The annual gas safety check is a legal duty for landlords of let homes
Example House | Fixed wiring | EICR | Every 5 years | BS 7671 and IET guidance |  |  |  | Interval may be shorter depending on use
Example House | Water system | Sentinel outlet temperature checks | Monthly | HSE ACOP L8 and HSG274
Example House | Water system | Legionella risk assessment review | Per risk assessment | HSE ACOP L8
Example House | Passenger lift | Thorough examination | Every 6 months | LOLER 1998 |  |  |  | Insurance engineer
Example House | Air conditioning over 12kW | TM44 energy inspection | Every 5 years | Energy Performance of Buildings Regulations